Response to Review — CSME 2026 paper

A pvlib-Based Computational Model of a Multi-Inverter Rooftop Photovoltaic Plant Driven by Public Weather Data: Sensitivity Analysis and Field Validation

C. N. Govino, W.-R. Yang — revision of 30 October 2026 (6 pages)

Summary of changes

The paper is now led by figures (13 figures, 3 tables, 5 pages). New: plant/measurement layout, three-phase waveforms, aliasing test, compact model chain, Sobol convergence, inverter structure vs efficiency, and clear days vs 3.5-year counters; new tables: factor ranges with confidence intervals and error metrics. Two conclusions changed: the budget reaches the clear-day measurement only at an implausible joint extreme, and over 3.5 years the inverter counters agree with the model within 3%, so the clear-day shortfall is not a permanent plant loss.

| Reviewer comment | Response and change | Where |
| --- | --- | --- |
| 1. Empirical validation is insufficient (about three months of data and a few short records). | Agreed; the field data remain limited and this is now stated as limitation (1). The raw Hioki recording did not run continuously, so no further measured days exist. Added a long-term check that needs no new measurement: the lifetime energy counters of the two 50 kW inverters (1280 days since commissioning). Compared with the model for the same calendar period, the counters are 0.8% and 2.7% higher (1411 and 1437 vs 1399 kWh/kWp/yr). The counters read about 3.0% above the recorder (checked on 18 Oct 2026). Conclusion changed: the 19% clear-day shortfall is not a permanent loss; the model is suitable for annual energy but not for hourly prediction on clear days. Suggested future data: monthly kWh of the Taipower sale meter and continuous logging. | Abstract; 4.5; Fig. 13; 5; 6 |
| 2. Irradiance from a station 21 km away; no on-site measurement, so discrepancies cannot be attributed to plant losses. | Agreed. No pyranometer exists on the roof, so this cannot be fixed with present data. The paper now says explicitly that the model error cannot be split into an irradiance part and a plant part, and names a plane-of-array pyranometer or reference cell as the most important next step. Mitigation already in the paper: only days with station clear-sky fraction > 0.9 are used for the bias; the hour-by-hour pattern and the February/October contrast argue against a constant station bias. | 2.2; 4.6; 5 (2) |
| 3. Measurement layout is not shown; thinning 2 ms → 10 ms must be validated for aliasing of the active power. | New Fig. 1: roof blocks, strings per MPPT, the three inverters, AC panel, recorder position and grid connection. New Fig. 2 (as sketched by the supervisor): three phase voltages of the bus, 120° apart, with rms and peak values; Eq. (1) P = √3·V_LL·I_L·cos φ and Eq. (2) two-wattmeter power. Text explains why Σ v_LL·i would give 1.5 P. Aliasing (new Fig. 3): explained why the mean power is preserved (samples at five equally spaced phases; whole-cycle intervals avoided) and tested with 400 synthetic minutes built from the measured unbalance, displacement and harmonics. Max error 0.06% (10 ms) and 0.05% (20 ms); 0.12% and 0.12% even at exactly 60 Hz; 200 ms would err by up to 12%. Note: the raw 2 ms files are not kept; if any are found, the same test can be repeated on real data with src/rev_aliasing.py adapted. | Fig. 1; Fig. 2; Fig. 3; 2.3 |
| 4. Sobol ranking depends on ranges and distributions; show convergence, convergence testing and confidence intervals. | Table 2 now gives the range, distribution and basis of every factor and states that the ranking depends on them (the ±10% GHI case shows the shift). Convergence (new Fig. 5b): base samples raised from 1,024 to 4,096 (45,056 runs) plus five extra scrambling seeds. Total indices change by at most 0.003 (±5%) and 0.003 (±10%); seed-to-seed SD ≤ 0.002; top-five ranking stable from 64 samples. Table 2 reports S_T with 95% bootstrap confidence intervals; the last four factors have indices below 0.005 and are not ranked. | 3 and 3.1; Table 2; Fig. 5 |
| 5. Distinguish differences in model structure from differences in assumed rated efficiency. | New Section 3.2 and Fig. 6. Same η: constant vs PVWatts differ by 0.36–0.37%; same peak efficiency: 0.6%; changing η from 0.985 to 0.96 within PVWatts: −2.6%. So the inverter effect in the budget is an efficiency assumption, not a structural one. On the clear October days the two structures with equal η differ by < 0.1%. | 3.2; Fig. 6; Abstract; 6 |
| 6. Clarify the 'stacked lower-bound assumption' and why options that would give lower output were excluded. | The reviewer is right: the earlier stack left out isotropic transposition (−3.9%) and Boland decomposition (−1.0%). Both are now included (Fig. 12; single effects given in the text). With every lower end the model reaches 82.0% of baseline, i.e. the measurement (81%) is reached. This changed the conclusion. The earlier sentence 'the remainder cannot be explained by the nine factors' was removed. New text: the budget reaches the measurement only at its joint extreme, which is implausible because (i) the isotropic model underestimates tilted irradiance on clear days [27], (ii) all lower ends together give −13.6% annually, far below the 5th percentile (−5.5%), and (iii) the same setting underestimates the clear day of 10 Feb by about 6%. | 4.4; Fig. 9; Fig. 12 |
| 7. High correlation but no accurate prediction; systematic overestimate of about 19% on clear days. | Agreed and stated directly: correlation shows only the shape; the level is wrong. The ratio is now defined explicitly as R = ΣP_actual / ΣP_model (Eq. 4). Table 3 now gives MBE, nMBE, RMSE, nRMSE and r for all five clear-sky records (nMBE +23% and +24%, nRMSE 27% and 31% in October). A leave-one-day-out test shows that a single correction factor does not transfer (factor from 17 Oct leaves −8.6% on 10 Feb and −19.7% on 7 Aug). The paper no longer claims predictive accuracy; it claims agreement in annual energy (counters) and a clear-day bias at hourly scale. | 4.2 (Eq. 4); Table 3; Fig. 10; 5; 6 |

Code for every new number: src/rev_sobol_convergence.py, src/rev_analysis.py, src/rev_aliasing.py, src/rev_fig_*.py; collected in paper_rev/numbers.json.